TECHNICAL SPECIFICATION

Simplex LBD Weld-Together

Radiator Load Bank System

DATE:

PROJECT:

Simplex LBD Weld-Together Radiator Load Bank designed for permanent installation indoors with the following features:

1.	GENERATOR LOAD BANK

1.1	General: An engine radiator airflow cooled, resistive load bank is required for permanent, on site installation as a component of a standby engine generator system. The load bank shall be designed for (remote, local), (automatic, manual) control.

1.2	Installation: The load bank shall be installed within the air outflow of the engine unit mounted radiator and shall be cooled by the radiator airflow. The load bank may be installed by one of the following methods:

1.2.1	Bolted attachment to radiator with duct and flex coupling to air outlet in wall.

1.2.2	Installation within air duct; flex transition to radiator and solid duct transition to air outlet in wall.

1.2.3	Bolted attachment to interior wall with duct and flex coupling to radiator.

1.2.4	Bolted attachment to exterior wall over air outlet. Load Bank should be weatherproof for this installation.

1.3	Electrical Connection: Power source to load bank connection is 3-phase, 3-wire plus ground. Additional control wire connections for remote control as required.

1.4	Load Bank Rating:

1.4.1	Capacity: _____  KW, 1.0 p.f.

1.4.2	Load Steps (5, 10, 20, 25, 40, 50) KW  load step resolution

1.4.3	Voltage: _____V AC, 3-ph., 3-W

1.4.4	Frequency: (50, 60, 400) Hertz

1.4.5	Air intake temperature: 155ºF maximum (radiator air outflow)

1.4.6	Airflow requirements: Radiator air outflow

1.4.7	Duty Cycle: Continuous

1.4-8	Air temp. rise: 100ºF, nominal

1.4.9	Air back pressure: .25-50" water column

1.5	Load Bank Design

1.5.1	General: The load bank shall be a completely self-contained unit which includes all resistive load elements, load control devices, load element branch circuit fuse protection, main load bus and terminals, control terminals, system protection devices and enclosure of required type.

1.5.2	The load bank shall be the manufacturer's standard product that has been investigated, tested and listed by Underwriters Laboratories or equivalent NRTL as a system.

1.5.3	Enclosure: Type (1,3R), welded sheet steel, UL approved finished painted consisting of an epoxy primer and a polyurethane top coat, consisting of a power section, for installation and wiring of the load elements and a control section for installation and wiring of control components. The control section is to be physically and thermally isolated from both the hot load elements and the heated airflow. Mounting adapters suitable for the installation method selected shall be supplied with the load bank. The exhaust of the load bank shall be screened and, if installed outdoors, louvers shall be provided.

1.5.4     Load elements: Load elements shall be UL listed, labeled or recognized, Simplex Powr Web Open wire,

helically wound, chromium alloy, thermally derated to 60%.  5% tolerance, 2% balance. .995 p.f. element wire

mechanically supported over entire length such that if a wire should break, the broken wire segments will not

short to adjacent conductors or to ground. Load elements are individually serviceable and replaceable in the

field without major disassembly of the load bank.

1.5.5	Load element short circuit protection: Branch circuit fuses, per each 50KW load branch circuit. Fuses shall be 200,000 A.I.C current limiting type.

1.5.6	Load control: One magnetic contactor per each fused branch circuit.

1.5.7	Load bank power wiring shall be 150ºC insulated.

1.5.8	Main terminals: Plated bus bar with a hole pattern to accept customer supplied cable

1.5.9	Control wiring shall be 105ºC insulated.

1.5.10	Control power shall be derived internally from the main load bus. Control and protective circuits shall operate at 120V via control power transformer or line-neutral circuit and shall be fused.

1.5.11	System protection: The load bank shall include a comprehensive protection system to protect against overheating. The system shall function to disconnect the load elements from the power source and activate an alarm upon sensing a loss of cooling airflow, or an exhaust air temperature greater than 300øF.

1.6	(Local, Remote) Control Panel

1.6.1	A Type (1,3R) control panel for (automatic, manual) operation shall be provided. The panel shall include:

1.6.2	Control power on-off push-buttons

1.6.3	"Normal operation" indicator lamp

1.6.4	Master load control switch

1.6.5	Load step control switches

1.6.6	"Cooling failure" alarm indicator lamp

1.6.7	Remote control panel shall be UL listed.

1.7	Warranty:  The load bank shall be supplied with a 2-year manufacturer's warranty which covers all materials and service labor.  The manufacturer shall demonstrate the availability of factory service technicians in support of the load bank.

1.8	Start-up Service:  The load bank manufacturer is to provide one day start-up service of the load bank, on site, after the load bank has been installed and connected.

1.9	Qualifications of load bank manufacturer

1.9.1	The load bank shall be a product of a firm regularly engaged in the design and manufacture of generator load banks.

1.9.2	The load bank manufacturer shall demonstrate at least five years experience with at least twenty-five successful installations of load banks similar or equal to the load bank specified herein.

1.9.3	The load bank manufacturer shall have an ISO certified quality/management system.

1.9.4	The load bank for this application shall be a Simplex LBD Series as manufactured by Simplex Inc., Springfield, Illinois.

ADD THE FOLLOWING SECTION TO PROVIDE FOR LOAD BANK OPERATION AS AN AUTOMATIC LOAD REGULATOR TO MAINTAIN A PRESET LOAD LEVEL

1.10	Automatic load bank controller

1.10.1	The load bank is to be equipped with an automatic controller which will be activated when the load bank mode control selector switch is placed in the "automatic" position.

1.10.2	In automatic mode, the load bank is to be on-line and continuously operative whenever the power source runs. The load bank shall provide a component of the total power source load and shall be automatically variable in response to dynamic total load demands upon the power source.

1.10.3	The automatic controller shall include control logic, solid-state sensors and time delays which shall act to apply/remove load bank component in multiple steps in response to dynamic output of the power source.

1.10.4	The automatic controller shall function to maintain total load upon the power source within a preset bandwidth by adding load bank load component as external load component drops and removing load bank component as external load rises.

1.10.5	The automatic controller shall sense load (amperes, kilowatts)

1.10.6	Full manual control of the load bank shall be restored when the mode selector switch is placed in the "manual" position.

1.10.7	The automatic controller shall include a solid-state load sensor with level and time delay adjustment and output contacts for each load step. A current transformer for external installation shall be provided.

ADD THE FOLLOWING SECTION TO PROVIDE FOR AUTOMATIC LOAD BANK OPERATION DURING A GENERATOR EXERCISE PERIOD

1.11	Automatic load step addition/subtraction

1.11.1	The load bank is to be equipped with a programmable logic controller (PLC) for automatic load step addition/subtraction which will be activated when the load bank mode control selector switch is placed in the "automatic" position.

1.11.2	In automatic mode, the load steps are initiated by a switch closure signal from generator exercise program (provided by the generator controller). Controller shall include provision for an adjustable delay between up/down steps and duration of test period length. Typical connection method is to provide contact closure from either the generator breaker or the ATS. Auto load step addition initiates on closures of this contact and ends on opening of contact. The contact opening then puts the load bank back into normal mode.

1.11.3	The automatic controller shall include control logic, solid-state sensors and time delays which shall act to apply/remove load bank component in sequential steps in during the generator exercise cycle.

1.11.4	Control power shall be 120v, single-phase from an external power source.