TECHNICAL SPECIFICATION

Simplex LBD Bolt-Together

Load Bank System

DATE:

PROJECT:

Simplex LBD Bolt-Together Radiator Load Bank designed for permanent installation (indoors/outdoors):

The load bank supplied shall be UL LISTED/LABELED with the following features:

Operational ratings and limitations as follows:

1.	Capacity:	_______ KW (400KW maximum), 1.0 power factor

2.	Voltage:                480V AC, 3- phase, 3- wire

3.	Frequency:	60 Hertz

4.	Load Steps:	KW step resolution

5.	Duty Cycle:	Continuous

6.	Temp. Rating:	180°F max. air intake temp.

60°-100°F nominal air temp. rise

7.	Airflow Req'd:	Radiator air outflow

8.	Altitude:	5500'  (higher, contact Simplex)

9.	Control Power:	Internal, from generator. 480V AC, single-phase. Fused circuits. Controls operate at 120V via control power transformer circuit.

Principle systems and components as follows:

1.	Load Elements:	Tubular type, weatherproof, totally enclosed, UL listed

2.	Load Control:	Branch circuit magnetic contactors

3.	Element Short

Circuit Protection:	Branch circuit fuses.  Fuses are 200KAIC, 600V, current limiting

4.	Power Wiring:	150°C, insulated, color coded

5.	Power Connection:	Barrier type power distribution block with line side compression terminals

6.	Control Wiring:	16AWG, 105°C

7.	Overheat Protection:	Sensor to detect high exhaust air temp above 300°F.  Circuits to disconnect load bank on overtemp.  Alarm contacts.

8.	Enclosure:	Type 1

Galvanized Steel Construction

Designed for permanent installation by mounting:

	Directly to engine radiator

	Within radiator air outflow duct

	On inside of wall over radiator air outlet

	On outside of wall over radiator air outlet

Load bank is designed to your radiator core, duct or outlet dimensions. Please specify.

Load bank control:

Local or Remote:

Manual

Control panel with control power on-off push-buttons master load control switch, load step switches, overtemp indicator, normal operation indicator. Internal control circuit and input terminals to dump load bank off-line on opening of remote control contacts.

Automatic

Automatic load leveling and load regulation to maintain total generator load within a preset bandwidth.  PLC controller senses generator load and automatically adds/subtracts load bank steps in order to maintain total generator load at a desired level.  Controller senses amperes.  Adjustable level and delay.  Control panel with control power on/off switch, manual/off/automatic load step switches, master load control switch, overtemp indicator and normal operation indicator.